ELEVATOR SUMP PUMP SYSTEM
The contractor shall furnish and install a Stancor Model SE-50-TV-RP complete pump and

Oil-Minder control system for each elevator pit, as shown on the drawings.  The system shall

be capable of pumping water automatically to the sewer and diverting oil to a storage 
container and shall include the oil diverting TV option.  The Oil-Minder System shall be
capable of sensing oil floating on the top of the water, emulsified in solution or solid oil and 
prevent the pump from discharging this oil into the sewer or storm drain.  The pump and oil
sensor technology control system must comply with TDLR elevator rules and ASME A 17.1
Section 2.2.2.5 (2007) standard.  The system shall function automatically to remove water
and water with any other substance from the pit automatically without any human

intervention.   The control system shall provide a local audible alarm with silence switch. 
Provide individual dry contacts for warning of conditions A, & B, C D, & E and panel 
mounted audible alarm with LED indicator lights for Power, Oil Detected and High water 
level.  The dry contacts shall be normally open and shall activate under the following 
conditions,  A) the presence of oil in the sump when the pump is signaled to run, B) high 
liquid level in the sump, C) high amps or a locked rotor motor condition, D) loss of electrical 
power to the panel, E) pump activation/pump run.  A dry contact closure that makes only in 
the event of a high liquid level condition and/or oil detected in the pit shall not be considered 
equal and will not be accepted.   Provide individual dry contacts and wire to the BMS for 
remote monitoring of Oil Detected and Diverted High Water Alarm.  Pump Run, Loss of 
Power & Locked Rotor/overload.  The Oil Monitoring Control System shall have a minimum 
of 15 years of proven reliability. Represented by Industrial Systems, Inc., 
Phone 1-800-460-0469.

The sump pump shall be a Model SE-50, heavy duty submersible type, capable of pumping water, water/oil and oil at a minimum capacity of 50 GPM @ 30’ TDH,   (3000 GPH )   as per ASME A 17.1 Section 2.2.2.5 (2007). The pump shall be built and tested to meet UL 778 standards and shall include thermal overload protection.  The motor shall be air filled and rated at 1/2 H.P., 
115 volt, 1 phase, 60 Hertz.  Oil filled motors are not considered equal.  The pump shall be capable of operating with the water level covering only 50% of the motor casing and shall operate automatically either continuously or intermittently, as required by the on-off float switch control.  The pump shall have a size 2” minimum discharge connection. The motor housing and fastening bolts shall be constructed of 304 Stainless Steel and the mechanical seals shall be housed in a separate oil-filled compartment.  The pump shall have a semi-open non-clogging Vortex impeller, and shall be designed for floor mounting complete with support legs.

The Solid State Oil Minder control system shall be built and tested to meet UL508 standards and shall be housed in a gasketed NEMA 4X electrical enclosure with a wiring terminal strip for field wiring to the J-Box in the hoistway.  The control panel shall include a field adjustable switch with variable Oil sensitivity settings, for indicating oil present, having an adjustable range of 1 to 10, factory set at #5 oil sensitivity and shall be capable of sensing emulsified oil and diverting it to a storage container for remediation.  The panel shall also include a separate over-current relay and field adjustable motor overload having a range of 5 to 15 amps, factory set at 8 amps for this pump application.  The control panel shall have a combination manual reset/push to test switch for motor overload with both automatic, manual reset and control diagnostics.  The control system must be factory set for automatic overload restart.  The factory installed Oil Sensor probe detection system must be hermetically sealed, heavy duty, Stainless Steel with low amperage self-cleaning technology.  The factory mounted and adjusted oil sensor-level probe shall be set no higher than 4” from the bottom of the pit.  The factory mounted main float switch will automatically start the pump on a level increase in the sump pit fluid level.  When the water or fluid level drops below the oil sensor probe tip the pump will automatically turn off.  The control panel shall provide a one (1) second time delay after the liquid level drops below the oil sensor probe tip, leaving about two inches of water in the pit.   At this point the oil sensor probe voltage will drop from 5VDC to 15 millivolts DC.    The oil sensor probe voltage shall not exceed 
15 millivolts DC until it comes in contact with water or any other fluid, at which point the oil sensor returns to 5VDC. The low 15 millivolt DC input shall reduce the potential field and subsequent metal ion exchange, preventing build up of foreign matter on the probe surface.  Oil sensing systems using floats, standard stainless steel probes or optical lens, subject to dirt contamination, high maintenance and false alarms are not considered equal.  If the main pump on float switch closes and the oil sensor measures a higher resistance than its set point, the pump is to be automatically started and the oil LED, audible alarm and remote alarm relay are to be energized.  The condition of oil present will automatically close the sewer valve and open the oil diverting valve.  The pump control float and oil sensing probe are to be factory mounted and positioned on the pump and factory tested as a complete system.  Pipe discharge field mounted pump on floats and field mounted oil sensors are not considered equal.   The control panel shall have a high decibel warning horn with illuminated red light complete with alarm silencing switch and separate dry contacts for each of the alarm events specified.  
The automatic electric control valves shall be a minimum size of 2” FPT, for this size pump, having a brass body with a minimum CV of 328, 1/4 turn ball valve, chrome plated brass ball with Teflon seats and adjustable packing, 400 psig, provide a NEMA 4X factory mounted enclosure, fast acting, three seconds or less, 115 volt AC motor actuator, output torque 300 in/lb with manual override, wiring terminal strip and valve position indicator.  The sewer discharge valve is to be in the normally open position and the oil diverting valve is to be in the normally closed position.  See piping detail on the plans.  Each control valve shall have control wires that are to be connected to the main control panel as per the manufacturers wiring diagram.
Install the electric control valves as shown on the plans.
The oil storage container shall have a capacity of 55 gallons as shown on the plans, furnished complete with a removable plain top cover having no connections.  The installing contractor shall field install all of the connections on the top drum cover with pipe sizes as shown or required.  Furnish and install a drum high fluid level alarm panel, NEMA 4 enclosure, 115/1/60 power, complete with weighted float switch with 20 feet of cord and a cord grip for mounting to the drum top.  The cord shall be both water proof and Oil Resistant.  The NEMA 4 alarm panel shall have a local audible and visual alarm, 85 DB, complete with silence switch and manual test button.  A set of dry alarm contacts shall be provided and wired to the BMS for remote drum high level alarm condition.  The storage container shall be mounted on a wheeled dolly for ease of remediation.  
The Oil-Minder Control system shall be provided with option RP (Remediation Provision) that consists of a deadman spring return Oil-Minder by-pass switch mounted on the control panel.  This deadman switch will allow the control panel to be manually overridden allowing the sump pump to pump oil out of the pit into the oil remediation container.  See the drawings for piping details and normal operating valve positions.  The normally closed oil diverter valve is to be installed in an easily accessible area, and piped to the oil storage container. The piping shall have unions for easy removal of the container for remediation. 
The control system shall include dual float switches for automatic pump activation and high water alarm.  The high water alarm float switch shall act as a redundant pump run (on) float in the event the primary pump run float being incapacitated.  Provide a clearly marked terminal board with the remote monitoring alarm contacts for connection to the BMS.  Provide a test button to test the pump operation and provide a means to check all of the alarm led lights, remote contacts and control diagnostic tests.
Provide a factory prewired NEMA 6 P water tight submersible junction box with a din rail mounted wiring terminal strip.  Provide factory installed wiring of pump, oil probe and floats into the NEMA 6 P junction box.  All cables between the pump and junction box shall be a maximum of 6’ long per NEC 2008.  The cable shall be heavy usage, water tight and oil resistant.  The floats and oil sensing probe shall be factory mounted on the pump housing.  All cable entries into the J-Box from the pump pit shall have NEMA 6 P water tight cord grips.
The control panel, pump, on/off float, high water alarm float, wiring, J-box and oil sensor probe shall be factory assembled as a complete assembly, ready to use system and shall be tested, for the intended purpose as a system, and certified by a nationally recognized independent testing laboratory such as ENTELA.  All of the equipment & components must be manufactured, assembled and tested in the USA, by the same company.  Individual components manufactured by different companies that are assembled to conform to this specification are not considered equal and will not be acceptable. 
Acceptable Manufacturers:

Stancor Pump Company, or Prior Approved Equal, provided all of the specifications are met.
END OF SECTION

STANCOR..SE-50.OIL.MINDER..TV.RP.SPECS.DOC.3-04-10..REV.17
PAGE  
1

